## Slide 1: Modbus Communication
Matthias Mersch
Automation of new EBC test hall

## Slide 2: Overview
Control of Belimo VAV/VVS valves
Modbus RTU protocol via RS485 interface
Implementation in Beckhoff TwinCAT 3 (structured text)
EL6021 terminal
PLC
TwinCAT 3
EL
6021
VAV/VVS 1
EtherCAT
VAV/VVS n
Modbus RTU

## Slide 3: Modbus Remote Terminal Unit (RTU) protocol
Serial communication  bit by bit
Master/Slave protocol
  One master, up to 32 slaves with unique address (1..247)
  Only master can initiate communication, slaves can only respond to requests
  Broadcast mode or communication with single slave
Slaves can store data in four different tables
Standard function codes to access tables
Data package
Table | Data Type | Access
Output Coils | Single bit | Read/Write
Input Coils | Single bit | Read-only
Input Registers | 16-bit unsigned | Read-only
Holding Registers | 16-bit unsigned | Read/Write
Device Address | Function Code | Data | Cyclic Redundancy Check
1 Byte | 1 Byte | n Bytes | 2 Bytes

## Slide 4: Hardware Components
Beckhoff EL6021 | Serial interface RS422/RS485
  Connection to PLC via E-bus coupler EK1100
  TxD and RxD communication channels, full/half duplex mode possible
  2400..115200 baud
  Number of data bits, parity, and stop bits variable
Up to 1000m twisted pair cable
  A maximum of 32 devices connected to terminal as daisy-chain
Termination resistors
  2 x 120Ω
  Between the two wires of the pair at both ends
Ground
Shield

## Slide 5: Electrical Wiring
Two-Wire EIA/TIS-485 (RS485)
  TxD+ and RxD+ pins are bridged to form D+ signal (not inverted)
  TxD- and RxD- pins are bridged to form D- signal (inverted)
  Common ground
Source: http://www.modbus.org/docs/Modbus_over_serial_line_V1.pdf
Termination resistors

## Slide 6: Software Requirements
Beckhoff TwinCAT 3 PLC (with Microsoft Visual Studio)
Tc2_ModbusRTU library

## Slide 7: CoE settings for EL6021 terminal
Set Baudrate (0x8000:11) to match slave (here 38.4 kBaud)
Set Data frame (0x800:15) to match slave (here 8N2)
  8 Data bits
  No parity
  2 stopbits
Enable half duplex (0x8000:06) (required for RS485 communication)  Add settings to startup list

## Slide 8: Process Data (PDO assignment)
Use 22x8 bit input, 22x8 bit output
  Inputs PDO Assignment 0x1A02 (Status + Data In [0..21])
  Outp PDO Assignment 0x1602 (Ctrl + Data Out [0..21])
Other options are 3x8 bit, 5x8 bit and 22x8 bit virtual COM

## Slide 9: Modbus RTU Library
Use function blocks from ModbusRTU library
  Here: ModbusRtuMaster_KL6x22B
    Modbus Master
    KL6xxx terminal
    22B process data interface
  Blocks for Modbus slaves and other process data interfaces available
Function blocks implement low-level serial communication according to Modbus RTU protocol
Input- and Output-Buffers are included
Function block actions implement the basic Modbus functions
  Reading and writing of coils/registers
Documentation: https://infosys.beckhoff.com/index.php?content=../content/1031/tcplclibmodbusrtu/9007199710009867.html&id=7075213495716034918

## Slide 10: Software Implementation (1/3)
Create instance of function block
Call Instance.<<Action>>
  Here, a register of the slave device is written
    UnitID is the modbus address of the slave [0..247, BYTE]
    MBAddr is the address of the register on the slave [0..9998, 0x0000..0x270E, WORD]
    Quantity is the number of registers to be written
    Data is an array of WORD, its size has to be according to Quantity
    Timeout should not be less than 5s to allow time for the slave to respond
    A rising edge of the Execute input (False -> True) starts the operation

## Slide 11: Software Implementation (2/3)
Wait for the process to finish
  Master has to finish one action before the next one can be started
  Call Instance.<<Action>> until master is not busy any more
    Execute needs to be false, because the action is already being performed
    Potential errors are monitored
 Other modbus functions can be implemented by using different actions

## Slide 12: Software Implementation (3/3)
State machine to control operation sequence and avoid errors/delays
Example:
  1. Step: Start writing setpoint
  2. Step: Finish writing process
  3. Step: Start reading current value
  4. Step: Finish reading current value
The PLC runs independent of the speed of the modbus communication
The master performs actions sequentially, no errors due to parallel requests

## Slide 13: IO links
Modbus master provides input and output structures
  InData
    Status (WORD)
    D (Array [0..21] of BYTE)
  OutData
    Ctrl (WORD)
    D (Array [0..21] of BYTE)
Variables are mapped to the inputs and outputs of the terminal
  Activate array mode to map D to Data [0..21]
 Activate Configuration after mapping is changed, components may not work properly after a simple download or online change

## Slide 14
Matthias Mersch
matthias.mersch@eonerc.rwth-aachen.de
matthias.mersch@rwth-aachen.de